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Tender / project name: ____________________
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1. Purpose and Basis
1.1 Purpose
This document responds to tender requirements for a LAN time server / GNSS-synchronized clock / NTP stratum-1 appliance, covering architecture, performance claims, interfaces, deployment, and acceptance recommendations for technical evaluation.
1.2 Basis
Purchaser’s tender documents (controlling text)
Shipping Product Specification Product Specification (Shipping)
One-pager Reference · Serve Policy · Capacity Selection Sheet (Reference · Policy · Capacity)
Bid-sanitized User Guide 用户指南（标书脱敏版） (do not attach the shipping edition that contains factory credentials)
Industrial Interface Protocol 工业接口协议附件
NTP RFC 5905 (server-side common subset as implemented)
Modbus RTU industrial practice (9600 8N1 slave)
1.3 Response Principles
Per-channel claims: NTP, RS-485 Modbus, TTL 1PPS, and IRIG-B120 metrics are independent and must not be cross-applied.
Testable: Contracted metrics should map to practical acceptance methods (Section 6).
Clear exclusions: Capabilities not implemented (PTP/IEEE 1588, dual-port redundancy, IPv6, NTS, etc.) are not claimed.

2. Understanding and Overall Solution
2.1 Typical Needs
	Consumer
	Typical need
	Channel

	Servers / PCs / NVR / switches
	LAN NTP
	RJ45 NTP

	PLC / SCADA / HMI
	Absolute time stamps
	RS-485 Modbus

	DAQ / scopes / sync nodes
	Hardware second edge
	TTL 1PPS

	Power / legacy timing gear
	IRIG-B
	IRIG-B120 DCLS



2.2 Technical Approach
GNSS 1PPS + local oscillator disciplining + RTC/SQW holdover + parallel multi-channel outputs:
Outdoor GNSS antenna
        │
        ▼
 GNSS module (1PPS + navigation data)
        │
        ▼
 Disciplining / phase monitor / state machine (LOCK / HOLDOVER)
        ├──► RJ45: NTP server + Web management
        ├──► RS-485: Modbus RTU absolute time
        ├──► TTL: 1PPS
        └──► IRIG-B120: DCLS timecode
After LOCK, the unit operates as an NTP Stratum 1 server. Brief GNSS loss enters Holdover with degrading quality over time (see Product Spec).
2.3 Evaluation Highlights
	Point
	Description

	Primary reference
	GNSS-based; not dependent on an upstream NTP server

	IT + OT in one box
	NTP plus Modbus / PPS / IRIG

	Operability
	Web Dashboard, LCD, event & 24h quality CSV export

	Traceability
	Factory SETID; firmware Build ID

	Compliant wording
	Accuracy stated per interface — no “10 ns over Ethernet” claim




3. Scope of Supply
3.1 Hardware
	No.
	Item
	Notes

	1
	QYTS-3000-BG-T-S time server
	Ethernet, RS-485, 1PPS, IRIG (this SKU)

	2
	GNSS antenna & cable (per contract)
	Outdoor, clear sky view

	3
	Power (single path `-S`, per contract / nameplate)
	One inlet at a time: (1) AC 220 V IEC 3-pin (onboard AC module); or (2) DC-IN (DC050-T) + external adapter (12–24 V DC). Never both; not dual-redundant `-D`

	4
	Shipping documents
	User guide, spec, protocol, wiring pack



Cabinet, switches, client software, and PLC engineering are by others unless contracted.
3.2 Firmware / Software
Factory firmware (version per nameplate / Web)
Built-in HTTP UI (Basic Auth)
NTP at boot; Modbus / 1PPS / IRIG per SKU

4. Key Technical Responses
4.1 Basics
	Common tender item
	Response

	Product class
	GNSS-disciplined LAN NTP time server

	Model
	QYTS-3000-BG-T-S

	Constellation / Osc / Power
	BG (BeiDou+GPS) / T (TCXO) / S (single supply)

	Protocol
	NTP v3/v4, UDP 123

	Network
	1× RJ45, 10/100M (single port; not dual-port HA)

	Default IP
	192.168.1.123/24, gw 192.168.1.1 (configurable)

	Management
	Web + front LCD

	Time reference
	GNSS 1PPS + TCXO discipline; industrial RTC (temp-compensated) / SQW holdover



4.2 Accuracy (Per Channel, after LOCK)
	Channel
	Typical claim
	Acceptance

	Internal / GNSS 1PPS reference
	Module short-term stability typically ≤ 10 ns RMS; internal jitter monitor typically ≤ 50 ns (short window)
	Lab / factory

	TTL 1PPS out
	Sub-µs edge vs internal PPS
	Scope / TIC

	RS-485 Modbus
	1 ms resolution (UTC incl. ms)
	PLC register compare

	Ethernet NTP
	Typical LAN millisecond class (measure at client)
	ntpq / chronyc / client logs

	Holdover
	Continues after brief GNSS loss; error grows with time
	Antenna-pull soak



Contract note: Internal “10 ns RMS” must not be equated to “10 ns NTP at the client” or “nanosecond Modbus.” Specify acceptance per interface.
4.3 NTP Capacity
	Item
	Response

	Role
	NTP server; typically Stratum 1 after LOCK

	Recommended clients
	≤ 60 on LAN

	Global replies
	Adaptive rate limit; overload protect ≈ ≤ 1024/s

	Per-source IP
	≤ 8/s

	ACL
	Optional NTP source whitelist

	Warm-up policy
	Optional Stratum-2 transitional replies via Web policy (factory default: reply when locked)



4.4 Industrial Interfaces
	Interface
	Response

	RS-485
	Modbus RTU slave, 9600 8N1, ID 0x01; FC 0x03/0x04; UTC with ms

	1PPS OUT
	TTL second pulse

	IRIG-B120
	DCLS, aligned to PPS second (this SKU)



Register map and bring-up: Industrial Interface Protocol.
4.5 Management & Logs
	Item
	Response

	Web
	Dashboard / Network; HTTP Basic Auth

	SNMP
	Read-only SNMPv2c / UDP 161 (b140+); no HTTPS / SNMPv3

	Event log
	`event_log.csv` (~2048-entry ring; default export ~latest 1024); Dashboard → Diagnostics → Export

	24h quality
	`quality_24h.csv`; hourly rows; `samples=0` = no GNSS-disciplined samples that hour

	LCD
	Inspection / decision / diagnosis / asset pages



4.6 Explicit Exclusions
Not in standard scope (unless a separate solution is bid):
PTP / IEEE 1588 and plant-wide sub-µs Ethernet timing
NTS, IPv6, NTP broadcast/multicast server
Dual Ethernet redundancy / failover
Nanosecond fieldbus timing
HTTPS, SNMPv3, SNMP write (on-device SNMP is v2c read-only only)

5. Integration Outline
5.1 IT (Network)
Connect to LAN (prefer management VLAN).
Set static IP; ensure UDP 123 reachability.
Point clients to device IP (`iburst` recommended).
Optional NTP source whitelist.
5.2 OT (Industrial)
RS-485 wiring per practice (120 Ω termination, common ground).
PLC/SCADA poll calendar registers (suggest ≥ 1 Hz) via FC03.
Edge sync → TTL 1PPS; legacy timecode → IRIG-B120.
5.3 Antenna
Outdoor clear sky; quality feedline; treat LOCK as prerequisite for official timing use.
5.4 Responsibility Split
	Party
	Scope

	Bidder (supply)
	Device, factory config, docs, training (per contract)

	Integrator
	Rack power, network design, PLC, bulk client config

	End user
	Patrol, antenna care, accounts / ACL




6. Suggested Acceptance
6.1 Incoming
Model, SETID, firmware Build vs packing list; power-on Web/LCD; SN visible.
6.2 Functional (suggested)
	No.
	Item
	Method
	Pass (suggested)

	1
	GNSS lock
	Antenna OK; LCD/Web
	LOCK / Stratum 1

	2
	NTP
	Same-subnet client
	Stable ms-class offset (site network dependent)

	3
	Modbus
	Master reads Y/M/D h:m:s.ms
	Matches reference within 1 ms resolution

	4
	1PPS
	Oscilloscope
	Stable second pulse

	5
	IRIG
	Receiver or scope
	Frame OK (if in contract)

	6
	Logs
	Download event_log / quality_24h from Dashboard Diagnostics
	Readable; quality includes hourly rows (incl. samples=0)



6.3 Accuracy Wording
Contract must name the acceptance interface. Do not apply internal 10 ns figures to NTP client tests.

7. Reliability & Operations
State machine visible on LCD/Web; Ethernet soft recovery paths and external-watchdog power-cycle strategy for hard faults (firmware policy); CSV logs for support; Web-configurable IP / NTP policy / ACL (see User Guide).

8. Implementation Schedule (Template)
	Phase
	Work
	Suggested duration

	T0
	Kickoff, IP/antenna plan
	3–5 working days

	T1
	Delivery & incoming inspection
	Per contract

	T2
	Install, power, cabling
	1–2 days / site

	T3
	Integration (NTP / PLC / timecode)
	1–3 days / site

	T4
	Training & handover
	0.5–1 day

	T5
	Trial run & final acceptance
	Per tender




9. Training & Warranty (Template)
Training: install notes, Web/LCD patrol, NTP & Modbus bring-up, log export + SETID/Build for support tickets.
	Item
	Fill per commercial terms

	Warranty
	____ years

	Support
	Phone / remote / on-site

	Spares
	________________




10. Clause-by-Clause Response Matrix (Template)
	No.
	Tender clause (summary)
	Bid response
	Status
	Evidence

	1
	NTP server
	UDP 123; Stratum 1 after LOCK
	Full
	Spec §5

	2
	GNSS timing
	GNSS 1PPS discipline
	Full
	Spec §1

	3
	Web management
	HTTP Basic Auth
	Full
	User Guide

	4
	RS-485 absolute time
	Modbus RTU, 1 ms
	Full
	Protocol annex

	5
	1PPS output
	TTL 1PPS
	Full
	Spec §7

	6
	IRIG-B
	IRIG-B120 DCLS (this SKU)
	Full
	Protocol annex

	7
	Dual-port redundancy
	Single port
	Deviation / N/A
	§4.6

	8
	PTP/1588
	Not included
	Deviation / N/A
	§4.6

	9
	…
	…
	…
	…




11. Deviation Statement (If Required)
For each deviation: clause ID, actual capability, mitigation/impact, and whether it is material (legal/commercial review).
Common proactive statement: This product is a single-port industrial NTP appliance and is not bid as a PTP plant-wide sub-µs solution. If PTP is mandatory, use a dedicated PTP design or consortium bid.

12. Attachment List
	No.
	Attachment
	Format
	Notes

	A1
	Product Specification (Shipping) ZH
	md/docx
	Product Specification (Shipping, ZH)

	A2
	Product Specification (Shipping) EN
	md/docx
	Product Specification (Shipping)

	A3
	Reference · Serve Policy · Capacity (One Page)
	md/docx
	Selection Sheet (Reference · Policy · Capacity)

	A4
	User Guide (bid-sanitized)
	md/docx
	用户指南（标书脱敏版） (not the shipping edition with factory password)

	A5
	Industrial Interface Protocol
	md
	工业接口协议附件

	A6
	This Bid Technical Proposal
	md/docx
	Bid Technical Proposal

	A6
	Datasheet / photos
	optional
	Commercial pack

	A7
	Test / factory reports
	optional
	Per contract



Packaging: Tender ZIP must contain only files from this public technical package. Do not include the shipping User Guide (factory credentials), internal unpublished technical materials.

13. Closing
QYTS-3000-BG-T-S addresses common industrial, security, office, and metering-assist needs for a local GNSS authority with multi-channel timing. The bidder affirms consistency with the shipping specification and protocol annex; acceptance is per channel; exclusions in §4.6 are not falsely claimed.
Commercial terms (price, delivery, warranty) are governed by the commercial bid volume.
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